## LV
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd. | POLE | FS/IS | ACB/MCCB | MCB | FAULT DUTY | Unnamed: 6 | Unnamed: 7 | Count
LV MDB REF : LV MDB -1 | [6 empty] | CONSULTANT : | 1
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
1 | INCOMER - 1 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA | 18
2 | INCOMER - 2 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY GENERATOR SUPPLIER | 17
1 | MDB-E1 | TP |  | 800 |  | 50 | FIRE PROOF | 18
2 | FIRE PUMP | TP |  | 320 |  | 50 | FIRE PROOF | 17
3 | SMDB-BN | TP |  | 500 |  | 50 | XLPE/SWA/PVC | 14
4 | SMDB-GN1 | TP |  | 350 |  | 50 | XLPE/SWA/PVC | 16
5 | SMDB-GN2A | TP |  | 630 |  | 50 | XLPE/SWA/PVC | 12
6 | SMDB-GN2B | TP |  | 500 |  | 50 | XLPE/SWA/PVC | 10
7 | SMDB-GN2C | TP |  | 630 |  | 50 | XLPE/SWA/PVC | 9
8 | SMDB-1N1 | TP |  | 400 |  | 50 | XLPE/SWA/PVC | 10
9 | DB-RMU | SP |  | 40 |  | 50 | XLPE/SWA/PVC | 10
9 | DB-TR | SP |  | 40 |  | 50 | XLPE/SWA/PVC | 10
10 | AHF PROVISION | TP |  | 400 |  | 50 |  | 9
11 | CAPACITOR BANK | TP |  | 1000 |  | 50 | XLPE/SWA/PVC | 6
LV MDB -1 | CONNECTED TO |  | TRANSFORMER #1 1500KVA |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
LV MDB REF : LV MDB -2 | [6 empty] | CONSULTANT : | 1
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
1 | INCOMER - 1 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA | 18
2 | INCOMER - 2 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY GENERATOR SUPPLIER | 17
1 | CHILLER-1 | TP |  | 800 |  | 50 | XLPE/SWA/PVC | 18
2 3 | CHILLER-2 CHILLER-3 | TP TP |  | 800 800 |  | 50 50 | XLPE/SWA/PVC XLPE/SWA/PVC | 1
3 | MCC-CHW | TP |  | 125 |  | 50 | XLPE/SWA/PVC | 14
4 | SMDB-RN | TP |  | 350 |  | 50 | XLPE/SWA/PVC | 16
13 | AHF PROVISION | TP |  | 400 |  | 50 |  | 9
14 | CAPACITOR BANK | TP |  | 1000 |  | 50 | XLPE/SWA/PVC | 8
LV MDB -2 | CONNECTED TO |  | TRANSFORMER #2 1500KVA |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1

## SMDB
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd. | POLE | FS/IS | ACB/MCCB | MCB | FAULT DUTY | Unnamed: 6 | Unnamed: 7 | Count
SMDB REF : | SMDB - BN | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 500 (N/A) |  | 30 | XLPE/SWA/PVC | 0
1 | DB-BN1 | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 18
2 | DB-BN2 | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 17
3 | POLISHING BAY | TP |  | 80 |  | 30 | XLPE/SWA/PVC | 14
4 | POLISHING BAY | TP |  | 80 |  | 30 | XLPE/SWA/PVC | 16
5 | USED OIL PUMP | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 12
6 | COMPRESSOR ROOM | TP |  | 80 |  | 30 | XLPE/SWA/PVC | 10
7 | CAR WASH | TP |  | 80 |  | 30 | XLPE/SWA/PVC | 9
8 | CAR WASH | TP |  | 80 |  | 30 | XLPE/SWA/PVC | 10
9 | SPARE | TP |  | 63 |  | 30 | -- | 10
SMDB - BN | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDB REF : | SMDB - BE1 | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 225 (N/A) |  | 35 | FIRE PROOF | 0
1 | DB-BE1 | TP |  | 40 |  | 35 | FIRE PROOF | 18
2 | CPEF | TP |  | 40 |  | 35 | FIRE PROOF | 17
3 | GEF | TP |  | 40 |  | 35 | FIRE PROOF | 14
4 | GMF | TP |  | 40 |  | 35 | FIRE PROOF | 16
5 | SEWAGE LIFT STAIOION -1 | TP |  | 32 |  | 35 | XLPE/SWA/PVC | 12
6 | TMF | TP |  | 32 |  | 35 | FIRE PROOF | 10
7 | TMF | TP |  | 32 |  | 35 | FIRE PROOF | 9
8 | TEF | TP |  | 32 |  | 35 | FIRE PROOF | 10
9 | TEF | TP |  | 32 |  | 35 | FIRE PROOF | 10
10 | SUMP PUMP | TP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
11 | JOCKEY PUMP | TP |  | 32 |  | 35 | FIRE PROOF | 6
12 | FIRE CIRCULATION PUMP | TP |  | 20 |  | 35 | FIRE PROOF | 5
SMDB REF : | SMDB - BE1 (CONT'D) | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 225 (N/A) |  | 35 | FIRE PROOF | 0
13 | SUMP PUMP | TP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
SMDB - BE1 | CONNECTED TO |  |  | MDB-E |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDB REF : | SMDB - BE2 | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 125 (N/A) |  | 30 | FIRE PROOF | 0
1 | DB-BE2 | TP |  | 40 |  | 30 | FIRE PROOF | 18
2 | WATER BOOSTER PUMP | TP |  | 32 |  | 30 | XLPE/SWA/PVC | 17
3 | SUMP PUMP-3 | TP |  | 20 |  | 30 | XLPE/SWA/PVC | 14
4 | SUMP PUMP-1 | TP |  | 20 |  | 30 | XLPE/SWA/PVC | 16
5 | SUMP PUMP-4 | TP |  | 20 |  | 30 | XLPE/SWA/PVC | 12
6 | SEWAGE PUMP | TP |  | 20 |  | 30 | XLPE/SWA/PVC | 10
7 | CPEF | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 9
8 | CPEF | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 10
SMDB - BE2 | CONNECTED TO |  |  | MDB-E |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDB REF : | SMDB - BE3 | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 200 (N/A) |  | 30 | FIRE PROOF | 0
1 | DB-UPS | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 18
2 | DB-MTR | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 17
3 | CBS PANEL | TP |  | 20 |  | 30 | FIRE PROOF | 14
4 | DX-2 | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 16
5 | CCU-1 | TP |  | 63 |  | 30 | XLPE/SWA/PVC | 12
6 | CCU-2 | TP |  | 63 |  | 30 | XLPE/SWA/PVC | 10
SMDB - BE3 | CONNECTED TO |  |  | MDB-E |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDB REF : | SMDB - GN1 | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 350 (N/A) |  | 30 | XLPE/SWA/PVC | 0
1 | DB-GN1 | TP |  | 100 |  | 30 | XLPE/SWA/PVC | 18
2 | DB-MN1 | TP |  | 63 |  | 30 | XLPE/SWA/PVC | 17
3 | SPARE | TP |  | 100 |  | 30 | -- | 14
4 | GARBAGE ROOM EQUIPMENT | TP |  | 20 |  | 30 | XLPE/SWA/PVC | 16
5 | EV CHARGING | TP |  | 63 |  | 30 | XLPE/SWA/PVC | 12
6 | QUICK SERVICE | TP |  | 40 |  | 30 | XLPE/SWA/PVC | 10
7 | QUICK SERVICE | SP |  | 32 |  | 30 | XLPE/SWA/PVC | 9
SMDB - GN1 | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDBREF : | SMDB-GE1 | [5 empty] | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 250 (N/A) |  | 35 | FIRE PROOF | 0
1 | DB-GE1 | TP |  | 40 |  | 35 | FIRE PROOF | 18
2 | DB-GE2 | TP |  | 40 |  | 35 | FIRE PROOF | 17
3 | DB-ME1 | TP |  | 40 |  | 35 | FIRE PROOF | 14
4 | DB-ME2 | TP |  | 40 |  | 35 | FIRE PROOF | 16
5 | DB-1E1 | TP |  | 40 | GE | 35 | FIRE PROOF | 12
6 | DB-1E2 | TP |  | 40 |  | 35 | FIRE PROOF | 10
7 | LIFT-1 | TP |  | 63 |  | 35 | FIRE PROOF | 9
8 | LIFT-2 | TP |  | 63 |  | 35 | FIRE PROOF | 10
9 | PANORAMIC LIFT | TP |  | 63 |  | 35 | FIRE PROOF | 10
10 | LIFT-1 CONTROL | SP |  | 20 |  | 35 | FIRE PROOF | 9
10 | LIFT-2 CONTROL | SP |  | 20 |  | 35 | FIRE PROOF | 9
10 | PANORAMIC LIFT CONTROL | SP |  | 20 |  | 35 | FIRE PROOF | 9
SMDBREF : | SMDB-GE1 (CONT'D) | [5 empty] | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 250 (N/A) |  | 35 | FIRE PROOF | 0
11 | WEPF | TP |  | 32 |  | 35 | FIRE PROOF | 6
12 | WEPF | TP |  | 32 |  | 35 | FIRE PROOF | 5
SMDB-GE1 | CONNECTED TO |  |  | MDB-E |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDBREF : |  | SMDB-GN2A |  |  |  |  | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 630 (N/A) |  | 35 | XLPE/SWA/PVC | 0
1 | DB-GN2 | TP |  | 80 |  | 35 | XLPE/SWA/PVC | 18
2 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 17
3 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 14
4 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 16
5 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 12
6 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
7 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 9
8 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
9 | EV CHARGER | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
10 | EV CHARGER | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 9
11 | EV CHARGER | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 6
12 | EV CHARGER | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 5
SMDBREF : | SMDB-GN2A (CONT'D) | [5 empty] | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 630 (N/A) |  | 35 | XLPE/SWA/PVC | 0
13 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
13 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
13 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
14 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 8
14 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 8
14 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 8
15 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 5
SMDB-GN2A | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDBREF : |  | SMDB-GN2B |  |  |  |  | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 500 (N/A) |  | 35 | XLPE/SWA/PVC | 0
1 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 18
2 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 17
3 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 14
4 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 16
5 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 12
6 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
7 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 9
8 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
9 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
10 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 9
11 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 6
12 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 5
SMDBREF : |  | SMDB-GN2B (CONT'D) |  |  |  |  | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 500 (N/A) |  | 35 | XLPE/SWA/PVC | 0
13 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
13 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
13 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
14 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 8
14 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 8
14 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 8
15 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 5
15 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 5
15 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 5
16 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 3
16 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 3
16 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 3
SMDB-GN2B |  | CONNECTED TO | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDBREF : |  | SMDB-GN2C |  |  |  |  | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 630 (N/A) |  | 35 | XLPE/SWA/PVC | 0
1 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 18
2 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 17
3 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 14
4 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 16
5 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 12
6 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 10
7 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 9
8 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 10
8 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 10
8 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 10
9 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 10
9 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 10
SMDBREF : | SMDB-GN2C (CONT'D) | [5 empty] | CONSULTANT : | 8
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 630 (N/A) |  | 35 | XLPE/SWA/PVC | 0
9 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 10
10 | BAY AREA | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
10 | QUICK SERVICE | SP |  | 20 |  | 35 | XLPE/SWA/PVC | 9
11 | CAR WASH | TP |  | 100 |  | 35 | XLPE/SWA/PVC | 6
12 | CAR WASH | TP |  | 100 |  | 35 | XLPE/SWA/PVC | 5
13 | QUICK SERVICE | TP |  | 63 |  | 35 | XLPE/SWA/PVC | 9
14 | DB-MN2 | TP |  | 40 |  | 35 | XLPE/SWA/PVC | 8
15 | DB-1N2 | TP |  | 40 |  | 35 | XLPE/SWA/PVC | 5
SMDB-GN2C | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1
SMDB REF : | SMDB - IN1 | [5 empty] | CONSULTANT : | 7
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
| INCOMER | TP |  | 400 (N/A) |  | 30 | XLPE/SWA/PVC | 0
1 | DB-1N1 | TP |  | 100 |  | 30 | XLPE/SWA/PVC | 18
2 | CAR LIFT | TP |  | 125 |  | 30 | XLPE/SWA/PVC | 17
3 | CAR LIFT | TP |  | 125 |  | 30 | XLPE/SWA/PVC | 14
4 | CAR LIFT CONTROL | SP |  | 20 |  | 30 | XLPE/SWA/PVC | 16
4 | CAR LIFT CONTROL | SP |  | 20 |  | 30 | XLPE/SWA/PVC | 16
4 | SPARE | SP |  | 80 |  | 30 | -- | 16
5 | EV CHARGER | TP |  | 63 |  | 30 | XLPE/SWA/PVC | 12
SMDB - IN1 | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 1

## DB
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd. | POLE | FS/IS | ACB/MCCB | MCB | FAULT DUTY | Unnamed: 6 | Unnamed: 7 | Count
MDB REF : |  | MDB - E |  |  |  |  | CONSULTANT : | 1
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | 20
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 20
1 | INCOMER - 1 | 4P |  | 800 (N/A) |  | 50 | XLPE/SWA/PVC | 18
2 | 550 KVA GENERATOR | 4P |  | 800 (N/A) |  | 50 | FIRE PROOF | 17
1 | SMDB-BE1 | TP |  | 225 |  | 50 | FIRE PROOF | 18
2 | SMDB-BE2 | TP |  | 125 |  | 50 | FIRE PROOF | 17
3 | SMDB-BE3 | TP |  | 200 |  | 50 | FIRE PROOF | 14
4 | SMDB-GE1 | TP |  | 250 |  | 50 | FIRE PROOF | 16
5 | SMDB-RE | TP |  | 40 |  | 50 | FIRE PROOF | 12
| MDB - E | CONNECTED TO | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE |  | 0
Type of Meter (Rating of Incomer) : | (1) UPTO 60A | (2) UPTO 125A | (3) LV CT ……….../………... | HV CT ……….../………...A |  |  |  | 1

## Others
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd. | Count | POLE | FS/IS | ACB/MCCB | MCB | FAULT DUTY | Unnamed: 6 | Unnamed: 7
FOR | 1
M/S. INTER EMIRATES MOTORS | 1
LOAD SCHEDULE | 1
R0 : December 05, 2023 (DETAIL DESIGN SUBMISSION) | 1
Prepared by | 1
Ian Banham & Associates | 1
P. O. Box: 23901 | 1
Dubai, U. A. E | 1
SR. | 20 | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE
NO | 20 | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC
1 | 18 | LV MDB - 1 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA
2 | 17 | LV MDB - 2 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA
MCCREF : | 1 | MCC- CHW | [5 empty] | CONSULTANT :
SR. | 20 | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE
NO | 20 | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC
| 0 | INCOMER | TP |  | 125 (N/A) |  | 30 | XLPE/SWA/PVC
1 | 18 | CHWP-1 | TP |  | 40 |  | 30 | XLPE/SWA/PVC
2 | 17 | CHWP-2 | TP |  | 40 |  | 30 | XLPE/SWA/PVC
3 | 14 | CHWP-3 | TP |  | 40 |  | 30 | XLPE/SWA/PVC
4 | 16 | PRESSURIZATION UNIT | TP |  | 20 |  | 30 | XLPE/SWA/PVC
MCC- CHW | 1 | CONNECTED TO |  | LV MDB-2 |  |  | TOTAL CONNECTED LOAD PER PHASE