## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 20
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : | B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING DETAILS OF CONNECTED LOAD/MAX. DEMAND
SMDB REF : | SMDB - IN1 | [5 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : ELECT ROOM
1ST FLOOR
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE (Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (3)
| INCOMER | TP |  | 400 (N/A) |  | 30 | XLPE/SWA/PVC |  | 4C 300 |  | 1C 150
OUTGOING
1 | DB-1N1 | TP |  | 100 |  | 30 | XLPE/SWA/PVC |  | 4C 35 |  | 1C 16 | 17.6 | 13.3 | 16.6 | 47.5 |  |  |  | *
2 | CAR LIFT | TP |  | 125 |  | 30 | XLPE/SWA/PVC |  | 4C 50 |  | 1C 25 | 18.33 | 18.33 | 18.33 | 55 |  |  |  | *
3 | CAR LIFT | TP |  | 125 |  | 30 | XLPE/SWA/PVC |  | 4C 50 |  | 1C 25 | 18.33 | 18.33 | 18.33 | 55 |  |  |  | *
4 | CAR LIFT CONTROL | SP |  | 20 |  | 30 | XLPE/SWA/PVC |  | 2C 4 |  | 1C 4 | 0.5 |  |  | 0.5 |  |  |  | *
4 | CAR LIFT CONTROL | SP |  | 20 |  | 30 | XLPE/SWA/PVC |  | 2C 4 |  | 1C 4 |  | 0.5 |  | 0.5 |  |  |  | *
4 | SPARE | SP |  | 80 |  | 30 | -- |  | -- |  | --
5 | EV CHARGER | TP |  | 63 |  | 30 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 7.33 | 7.33 | 7.33 | 22 |  |  |  | *
SMDB - IN1 | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 62.1 | 57.8 | 60.6 | 180.5 |  |  |  | TOTAL
DEMAND FACTOR…… MAX. DEMAND…...…kW TOTAL CONNECTED LOAD (3 PHASE)…180.50…kW TOTAL BUILD - UP AREA ......... ACTUAL LOAD (3 PH)…...kW
| CONSULTANTS : M/S. IAN BANHAM AND ASSOCIATES | [9 empty] | TEL : 04 - 370 5777 |  |  |  | FAX : 04 - 370 5888
| Type of Meter (Rating of Incomer) : |  |  |  | (1) UPTO 60A |  |  | (2) UPTO 125A |  |  | (3) LV CT | ……….../………... |  |  | HV CT ……….../………...A
[5 empty] | (1 PHASE) |  |  | (3 PHASE)
* REFER SINGLE LINE DIAGRAM FOR ELCB RATING