## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 7
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : | B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING DETAILS OF CONNECTED LOAD/MAX. DEMAND
SMDB REF : | SMDB - BE1 | [5 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : ELECT ROOM
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE (Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (4)
| INCOMER | TP |  | 225 (N/A) |  | 35 | FIRE PROOF |  | 4C 120 |  | 1C 70
OUTGOING
1 | DB-BE1 | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 5.3 | 4.2 | 4.3 | 13.8 |  |  |  | *
2 | CPEF | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 5.33 | 5.33 | 5.33 | 16 |  |  |  | *
3 | GEF | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 5.5 | 5.5 | 5.5 | 16.5 |  |  |  | *
4 | GMF | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 5.5 | 5.5 | 5.5 | 16.5 |  |  |  | *
5 | SEWAGE LIFT STAIOION -1 | TP |  | 32 |  | 35 | XLPE/SWA/PVC |  | 4C 6 |  | 1C 6 | 0.5 | 0.5 | 0.5 | 1.5 |  |  |  | *
6 | TMF | TP |  | 32 |  | 35 | FIRE PROOF |  | 4C 6 |  | 1C 6 | 2.33 | 2.33 | 2.33 | 7 |  |  |  | *
7 | TMF | TP |  | 32 |  | 35 | FIRE PROOF |  | 4C 6 |  | 1C 6 | 2.33 | 2.33 | 2.33 | 7 |  |  |  | *
8 | TEF | TP |  | 32 |  | 35 | FIRE PROOF |  | 4C 6 |  | 1C 6 | 2.33 | 2.33 | 2.33 | 7 |  |  |  | *
9 | TEF | TP |  | 32 |  | 35 | FIRE PROOF |  | 4C 6 |  | 1C 6 | 2.33 | 2.33 | 2.33 | 7 |  |  |  | *
10 | SUMP PUMP | TP |  | 20 |  | 35 | XLPE/SWA/PVC |  | 4C 4 |  | 1C 4 | 0.5 | 0.5 | 0.5 | 1.5 |  |  |  | *
11 | JOCKEY PUMP | TP |  | 32 |  | 35 | FIRE PROOF |  | 4C 6 |  | 1C 6 | 2.17 | 2.17 | 2.17 | 6.5 |  |  |  | *
12 | FIRE CIRCULATION PUMP | TP |  | 20 |  | 35 | FIRE PROOF |  | 4C 4 |  | 1C 4 | 1.83 | 1.83 | 1.83 | 5.5 |  |  |  | *
CONT'D…