## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 12
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : | B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING DETAILS OF CONNECTED LOAD/MAX. DEMAND
SMDBREF : | SMDB-GE1 | [5 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : ELECT ROOM
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE (Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (4)
| INCOMER | TP |  | 250 (N/A) |  | 35 | FIRE PROOF |  | 4C 150 |  | 1C 70
OUTGOING
1 | DB-GE1 | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 4.3 | 3.7 | 2.1 | 10.1 |  |  |  | *
2 | DB-GE2 | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 4 | 3.4 | 2.6 | 10 |  |  |  | *
3 | DB-ME1 | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 2.8 | 2.7 | 2.9 | 8.4 |  |  |  | *
4 | DB-ME2 | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 2.8 | 3 | 3.2 | 9 |  |  |  | *
5 | DB-1E1 | TP |  | 40 | GE | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 4.4 | 3.7 | 4.1 | 12.2 |  |  |  | *
6 | DB-1E2 | TP |  | 40 |  | 35 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 1.6 | 1.6 | 0.5 | 3.7 |  |  |  | *
7 | LIFT-1 | TP |  | 63 |  | 35 | FIRE PROOF |  | 4C 16 |  | 1C 16 | 5 | 5 | 5 | 15 |  |  |  | *
8 | LIFT-2 | TP |  | 63 |  | 35 | FIRE PROOF |  | 4C 16 |  | 1C 16 | 5 | 5 | 5 | 15 |  |  |  | *
9 | PANORAMIC LIFT | TP |  | 63 |  | 35 | FIRE PROOF |  | 4C 16 |  | 1C 16 | 5 | 5 | 5 | 15 |  |  |  | *
10 | LIFT-1 CONTROL | SP |  | 20 |  | 35 | FIRE PROOF |  | 2C 4 |  | 1C 4 | 0.5 |  |  | 0.5 |  |  |  | *
10 | LIFT-2 CONTROL | SP |  | 20 |  | 35 | FIRE PROOF |  | 2C 4 |  | 1C 4 |  | 0.5 |  | 0.5 |  |  |  | *
10 | PANORAMIC LIFT CONTROL | SP |  | 20 |  | 35 | FIRE PROOF |  | 2C 4 |  | 1C 4 |  |  | 0.5 | 0.5 |  |  |  | *
CONT'D…