## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 16
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : |  | B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING DETAILS OF CONNECTED LOAD/MAX. DEMAND
SMDBREF : |  | SMDB-GN2B |  |  |  |  | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : ELECT ROOM
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE (Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (4)
| INCOMER | TP |  | 500 (N/A) |  | 35 | XLPE/SWA/PVC |  | 2x4C 150 |  | 2x1C 70
OUTGOING
1 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
2 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
3 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
4 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
5 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
6 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
7 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
8 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
9 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
10 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
11 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
12 | BAY AREA | TP |  | 63 |  | 35 | XLPE/SWA/PVC |  | 4C 16 |  | 1C 16 | 6 | 6 | 6 | 18
CONT'D…