## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 2
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT :B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING | [6 empty] | DETAILS OF CONNECTED LOAD/MAX. DEMAND | [7 empty] | AREA : |  |  | AL QUOZ FIRST, DUBAI
PLANNED COMPLETION DATE : 2024 | [6 empty] | OWNER : |  | M/S. INTER EMIRATES MOTORS | [5 empty] | PLOT : |  |  | 35410013
LV MDB REF : LV MDB -1 | [6 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : |  |  | LV ROOM
BASEMENT FLOOR
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE(Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HVCT (3)
1 | INCOMER - 1 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA |  |  |  | 2x1C 150 | [6 empty] | 1 | 2400/5A CTM
2 | INCOMER - 2 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY GENERATOR SUPPLIER |  |  |  | PROVISION FOR MOBILE GENERATOR WITH ELECTRICAL AND MECHANICAL INTERLOCK
| OUTGOING |  | (D.O.T)
1 | MDB-E1 | TP |  | 800 |  | 50 | FIRE PROOF |  | 2x4C 300 |  | 2x1C 150 | 132.77 | 130.67 | 125.17 | 388.6 | 550 KVA GENERATOR
2 | FIRE PUMP | TP |  | 320 |  | 50 | FIRE PROOF |  | 4C 185 |  | 1C 95 | 42 | 42 | 42 | 126 |  |  |  | *
3 | SMDB-BN | TP |  | 500 |  | 50 | XLPE/SWA/PVC |  | 2x4C 150 |  | 2x1C 70 | 76.9 | 74.3 | 73.7 | 224.9
4 | SMDB-GN1 | TP |  | 350 |  | 50 | XLPE/SWA/PVC |  | 4C 240 |  | 1C 120 | 55.33 | 54.63 | 53.83 | 163.8
5 | SMDB-GN2A | TP |  | 630 |  | 50 | XLPE/SWA/PVC |  | 2x4C 185 |  | 2x1C 95 | 88.23 | 84.73 | 85.03 | 258
6 | SMDB-GN2B | TP |  | 500 |  | 50 | XLPE/SWA/PVC |  | 2x4C 150 |  | 2x1C 70 | 78 | 78 | 78 | 234
7 | SMDB-GN2C | TP |  | 630 |  | 50 | XLPE/SWA/PVC |  | 2x4C 185 |  | 2x1C 95 | 87.67 | 87.47 | 85.57 | 260.7
8 | SMDB-1N1 | TP |  | 400 |  | 50 | XLPE/SWA/PVC |  | 4C 300 |  | 1C 150 | 62.1 | 57.8 | 60.6 | 180.5
9 | DB-RMU | SP |  | 40 |  | 50 | XLPE/SWA/PVC |  | 2C 10 |  | 1C 10 | 1.8 |  |  | 1.8 |  |  |  | *
9 | DB-TR | SP |  | 40 |  | 50 | XLPE/SWA/PVC |  | 2C 10 |  | 1C 10 |  | 2 |  | 2 |  |  |  | *
10 | AHF PROVISION | TP |  | 400 |  | 50 |  |  | -- |  | -- | [7 empty] | *
11 | CAPACITOR BANK | TP |  | 1000 |  | 50 | XLPE/SWA/PVC |  | 3x4C 300 |  | 3X1C 150 | 350 kVAR CAPACITOR BANK"
LV MDB -1 | CONNECTED TO |  | TRANSFORMER #1 1500KVA |  |  | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 624.8 | 611.6 | 603.9 | 1840.3 |  |  | 1 | TOTAL
DEMAND FACTOR…0.70… MAX. DEMAND…1,200.01…kW TOTAL CONNECTED LOAD (3 PHASE)…1,840.30…kW TOTAL BUILD - UP AREA ......... ACTUAL LOAD (3 PH)…1,714.30...kW
| CONSULTANTS : M/S. IAN BANHAM AND ASSOCIATES | [9 empty] | TEL : 04 - 370 5777 |  |  |  | FAX : 04 - 370 5888
| Type of Meter (Rating of Incomer) : |  |  |  | (1) UPTO 60A |  |  | (2) UPTO 125A |  |  | (3) LV CT | ……….../………... |  |  | HV CT ……….../………...A
[5 empty] | (1 PHASE) |  |  | (3 PHASE)
* REFER SINGLE LINE DIAGRAM FOR ELCB RATING