## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 3
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT :B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING | [6 empty] | DETAILS OF CONNECTED LOAD/MAX. DEMAND | [7 empty] | AREA : |  |  | AL QUOZ FIRST, DUBAI
PLANNED COMPLETION DATE : 2024 | [6 empty] | OWNER : |  | M/S. INTER EMIRATES MOTORS | [5 empty] | PLOT : |  |  | 35410013
LV MDB REF : LV MDB -2 | [6 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : |  |  | LV ROOM
BASEMENT FLOOR
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE(Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HVCT (3)
1 | INCOMER - 1 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA |  |  |  | 2x1C 150 | [6 empty] | 1 | 2400/5A CTM
2 | INCOMER - 2 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY GENERATOR SUPPLIER |  |  |  | PROVISION FOR MOBILE GENERATOR WITH ELECTRICAL AND MECHANICAL INTERLOCK
| OUTGOING |  | (D.O.T)
1 | CHILLER-1 | TP |  | 800 |  | 50 | XLPE/SWA/PVC |  | 2x4C 300 |  | 2x1C 150 | 103.33 | 103.33 | 103.33 | 310 |  | DUTY CHILLER
2 3 | CHILLER-2 CHILLER-3 | TP TP |  | 800 800 |  | 50 50 | XLPE/SWA/PVC XLPE/SWA/PVC |  | 2x4C 300 2x4C 300 |  | 2x1C 150 2x1C 150 | 103.33 103.33 | 103.33 103.33 | 103.33 103.33 | 310.00 310.00 | DUTY CHILLER +STAND BY CHILLER WITH E/M INTERLOCK
3 | MCC-CHW | TP |  | 125 |  | 50 | XLPE/SWA/PVC |  | 4C 50 |  | 1C 25 | 18.5 | 18.5 | 18.5 | 55.5 | STAND BY LOAD 17.5KW
4 | SMDB-RN | TP |  | 350 |  | 50 | XLPE/SWA/PVC |  | 4C 240 |  | 1C 120 | 57.97 | 57.77 | 57.47 | 173.2
13 | AHF PROVISION | TP |  | 400 |  | 50 |  |  | -- |  | -- | [7 empty] | *
14 | CAPACITOR BANK | TP |  | 1000 |  | 50 | XLPE/SWA/PVC |  | 3x4C 300 |  | 3X1C 150 | 350 kVAR CAPACITOR BANK"
LV MDB -2 | CONNECTED TO |  | TRANSFORMER #2 1500KVA |  |  | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 386.47 | 386.27 | 385.97 | 1158.7 |  |  | 1 | TOTAL
| DEMAND FACTOR…1.00… MAX. DEMAND…831.20…kW |  |  |  |  | TOTAL CONNECTED LOAD (3 PHASE)…1,158.70…kW TOTAL BUILD - UP AREA ......... ACTUAL LOAD (3 PH)…831.20...kW
| CONSULTANTS : M/S. IAN BANHAM AND ASSOCIATES | [9 empty] | TEL : 04 - 370 5777 |  |  |  | FAX : 04 - 370 5888
| Type of Meter (Rating of Incomer) : |  |  |  | (1) UPTO 60A |  |  | (2) UPTO 125A |  |  | (3) LV CT | ……….../………... |  |  | HV CT ……….../………...A
[5 empty] | (1 PHASE) |  |  | (3 PHASE)
* REFER SINGLE LINE DIAGRAM FOR ELCB RATING