## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 6
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : | B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING DETAILS OF CONNECTED LOAD/MAX. DEMAND
SMDB REF : | SMDB - BN | [5 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : ELECT ROOM
BASEMENT
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE (Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (3)
| INCOMER | TP |  | 500 (N/A) |  | 30 | XLPE/SWA/PVC |  | 2x4C 150 |  | 1C 150
OUTGOING
1 | DB-BN1 | TP |  | 40 |  | 30 | XLPE/SWA/PVC |  | 4C 10 |  | 1C 10 | 3.7 | 3 | 2.4 | 9.1 |  |  |  | *
2 | DB-BN2 | TP |  | 40 |  | 30 | XLPE/SWA/PVC |  | 4C 10 |  | 1C 10 | 5.2 | 3.3 | 3.3 | 11.8 |  |  |  | *
3 | POLISHING BAY | TP |  | 80 |  | 30 | XLPE/SWA/PVC |  | 4C 25 |  | 1C 16 | 12 | 12 | 12 | 36 |  |  |  | *
4 | POLISHING BAY | TP |  | 80 |  | 30 | XLPE/SWA/PVC |  | 4C 25 |  | 1C 16 | 12 | 12 | 12 | 36 |  |  |  | *
5 | USED OIL PUMP | TP |  | 40 |  | 30 | XLPE/SWA/PVC |  | 4C 10 |  | 1C 10 | 2 | 2 | 2 | 6 |  |  |  | *
6 | COMPRESSOR ROOM | TP |  | 80 |  | 30 | XLPE/SWA/PVC |  | 4C 25 |  | 1C 16 | 11 | 11 | 11 | 33 |  |  |  | *
7 | CAR WASH | TP |  | 80 |  | 30 | XLPE/SWA/PVC |  | 4C 25 |  | 1C 16 | 11 | 11 | 11 | 33 |  |  |  | *
8 | CAR WASH | TP |  | 80 |  | 30 | XLPE/SWA/PVC |  | 4C 25 |  | 1C 16 | 11 | 11 | 11 | 33 |  |  |  | *
9 | SPARE | TP |  | 63 |  | 30 | -- |  | -- |  | -- | 9 | 9 | 9 | 27
SMDB - BN | CONNECTED TO |  | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 76.9 | 74.3 | 73.7 | 224.9 |  |  |  | TOTAL
DEMAND FACTOR…… MAX. DEMAND…...…kW TOTAL CONNECTED LOAD (3 PHASE)…224.90…kW TOTAL BUILD - UP AREA ......... ACTUAL LOAD (3 PH)…...kW
| CONSULTANTS : M/S. IAN BANHAM AND ASSOCIATES | [9 empty] | TEL : 04 - 370 5777 |  |  |  | FAX : 04 - 370 5888
| Type of Meter (Rating of Incomer) : |  |  |  | (1) UPTO 60A |  |  | (2) UPTO 125A |  |  | (3) LV CT | ……….../………... |  |  | HV CT ……….../………...A
[5 empty] | (1 PHASE) |  |  | (3 PHASE)
* REFER SINGLE LINE DIAGRAM FOR ELCB RATING