## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 1
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING | [6 empty] | DETAILS OF CONNECTED LOAD/MAX. DEMAND | [6 empty] | AREA : |  |  | AL QUOZ FIRST, DUBAI
PLANNED COMPLETION DATE : 2024 | [6 empty] | OWNER : |  | M/S. INTER EMIRATES MOTORS |  |  |  |  | PLOT : |  |  | 35410013
SUMMARY | [6 empty] | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | ECC | MAXIMUM |  |  |  | CONNECTED LOAD - KW |  |  | KWH METER | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | SIZE - 1C mm² | DEMAND kW | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (3)
INCOMER
OUTGOING
1 | LV MDB - 1 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA |  |  | 2x1C 150 | 1200.01 | 624.8 | 611.6 | 603.9 |  |  | 1840.3 | 1 | 2400/5A CTM
2 | LV MDB - 2 | 4P | 2500 SET @ 0.85 |  |  | 50 | BY DEWA |  |  | 2x1C 150 | 831.2 | 386.47 | 386.27 | 385.97 |  |  | 1158.7 | 1 | 2400/5A CTM
50
[6 empty] | TOTAL CONNECTED LOAD PER PHASE |  |  |  |  | 2031.21 | 1011.27 | 997.87 | 989.87 |  |  | 2999 | 2 | TOTAL
DEMAND FACTOR…0.68… MAX. DEMAND…2,031.21…kW TOTAL CONNECTED LOAD (3 PHASE)…2,999.00…kW TOTAL BUILD - UP AREA ......... ACTUAL LOAD (3 PH)…2,999.00...kW
| CONSULTANTS : M/S. IAN BANHAM AND ASSOCIATES | [9 empty] | TEL : 04 - 370 5777 |  |  | FAX : 04 - 370 5888
| Type of Meter (Rating of Incomer) : |  |  |  | (1) UPTO 60A |  |  | (2) UPTO 125A |  |  | (3) LV CT |  |  | ……….../………... | HV CT ……….../………...A
[5 empty] | (1 PHASE) |  |  | (3 PHASE)
REV. | DATE
0 | December 05, 2023