## Sheet1
Evaluation Only. Created with Aspose.PDF. Copyright 2002-2024 Aspose Pty Ltd.
PAGE - SCH - 4
IAN BANHAM & ASSOCIATES | ELECTRICAL
PROJECT : | B+G+M+1 FLOOR CAR SHOWROOM & OFFICE BUILDING DETAILS OF CONNECTED LOAD/MAX. DEMAND
MDB REF : |  | MDB - E |  |  |  |  | CONSULTANT : |  | M/S. IAN BANHAM & ASSOCIATES | [5 empty] | LOCATION : LV ROOM
BASEMENT FLOOR
SR. | CIRCUIT | SP/ | RATING - AMPS |  |  | FAULT | PVC/XLPE | CABLE SIZE |  | LENGTH | ECC | CONNECTED LOAD - KW |  |  |  | KWH METER |  |  | REMARKS
NO | FEEDER DB NO. | TP | ACB | MCCB | MCB | DUTY KA | SWA/PVC/SC | 2/4x1C mm² | 2/3/4C mm² | OF CABLE (Mtrs) | SIZE -1C mm² | R-PHASE kW | Y-PHASE kW | B-PHASE kW | TOTAL kW | 1 Ph (1) | 3 Ph (2) | LV/HV CT (3)
1 | INCOMER - 1 | 4P |  | 800 (N/A) |  | 50 | XLPE/SWA/PVC |  | 2x4C 300 |  | 1C 300
2 | 550 KVA GENERATOR | 4P |  | 800 (N/A) |  | 50 | FIRE PROOF |  | 2x4C 300 |  | 1C 300
OUTGOING
1 | SMDB-BE1 | TP |  | 225 |  | 50 | FIRE PROOF |  | 4C 120 |  | 1C 70 | 36.47 | 35.37 | 35.47 | 107.3
2 | SMDB-BE2 | TP |  | 125 |  | 50 | FIRE PROOF |  | 4C 50 |  | 1C 25 | 18.37 | 17.87 | 18.07 | 54.3
3 | SMDB-BE3 | TP |  | 200 |  | 50 | FIRE PROOF |  | 4C 95 |  | 1C 50 | 29.47 | 30.77 | 27.87 | 88.1
4 | SMDB-GE1 | TP |  | 250 |  | 50 | FIRE PROOF |  | 4C 150 |  | 1C 70 | 42.07 | 40.27 | 37.57 | 119.9
5 | SMDB-RE | TP |  | 40 |  | 50 | FIRE PROOF |  | 4C 10 |  | 1C 10 | 6.4 | 6.4 | 6.2 | 19
| MDB - E | CONNECTED TO | LV MDB-1 |  |  | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 132.77 | 130.67 | 125.17 | 388.6 |  |  |  | TOTAL
DEMAND FACTOR…… MAX. DEMAND…...…kW TOTAL CONNECTED LOAD (3 PHASE)…388.60…kW TOTAL BUILD - UP AREA ......... ACTUAL LOAD (3 PH)…...kW
| CONSULTANTS : M/S. IAN BANHAM AND ASSOCIATES | [9 empty] | TEL : 04 - 370 5777 |  |  |  | FAX : 04 - 370 5888
Type of Meter (Rating of Incomer) : | (1) UPTO 60A | (2) UPTO 125A | (3) LV CT ……….../………... | HV CT ……….../………...A
| (1 PHASE) | (3 PHASE)